# Street lighting tender specification

Template from OpenSLMS Learn. Text in [square brackets] is for you to complete. Orange italic notes give regional options; delete the ones that do not apply. Check every clause with your technical, procurement, and legal teams.

# 1. Scope

The contractor shall supply, install, commission, and maintain [number] LED road luminaires, [number] cabinet controllers, [number] lamp-level nodes, and a central management and maintenance platform for [city / authority], for a period of [years] years.

# 2. Standards and compliance

All equipment shall comply with the current editions of the following, or equivalent:

Europe: EN 13201 (lighting design), EN 60598-1 and EN 60598-2-3, EN 62722-2-1, EN 61347, EN 62471, CE marking (LVD, EMC, RED, RoHS, Ecodesign), ENEC or equivalent independent certification.

Middle East: [authority] road lighting manual, IEC 60598-2-3, IEC 62722-2-1, IEC 61547, local conformity (ECAS / EQM, SASO via SABER, or GSO), and the authority approved product list.

South Asia: IS 1944, IS 10322, IS 16101–16108 series, BIS Compulsory Registration, test reports from an NABL-accredited laboratory.

USA: ANSI/IES RP-8, UL 1598 and UL 8750 listing by an NRTL, ANSI C136 series (C136.37, C136.41), FCC Part 15, DLC Qualified Products List, NEC (NFPA 70).

# 3. Lighting performance

The bidder shall submit a lighting calculation for each road type in Annex A, using the photometric file of the offered luminaire.

Each road shall meet the lighting class in Annex A with a maintenance factor of [value].

The bidder shall state the power density indicator (PDI) and annual energy consumption indicator (AECI) per EN 13201-5 for each design.

Uplight: [ULOR 0% / BUG U0]. Glare: [class or threshold increment limit].

CCT: [3000 K residential / 4000 K main roads]. CRI: 70 or more.

# 4. Luminaire

Luminous efficacy of the complete luminaire: [130] lm/W or more, measured to LM-79 or EN 13032-4.

Lifetime: [L80B10] at [100,000] hours, supported by LM-80 data and a TM-21 projection.

Ingress protection IP66; impact protection IK08 or better.

Surge protection: [10] kV differential and common mode, with status indication.

Rated ambient temperature: [−30 °C to +50 °C].

Driver: programmable, with constant light output, stand-alone dimming profile, and [DALI-2 / D4i / 0–10 V] interface.

Controller socket on every luminaire, whether or not nodes are supplied:

Europe: Zhaga Book 18 with Zhaga-D4i certification.  Middle East / South Asia: NEMA 7-pin (ANSI C136.41) or Zhaga Book 18, as specified.  USA: NEMA 7-pin (ANSI C136.41).

Driver and LED module shall be replaceable on site with standard tools.

Warranty: [5 / 10] years on the complete luminaire, including driver and surge protector.

# 5. Controllers and network

Cabinet controllers shall measure voltage, current, power, energy, and power factor for each phase, and switch each circuit.

Lamp-level nodes shall switch and dim each luminaire and report energy, burn hours, and faults.

Controllers shall store schedules locally and keep operating if the network or platform is not available.

Communication: [LTE-M / NB-IoT / LoRaWAN / Wi-SUN / RF mesh]. The bidder shall show coverage on site before award.

Interoperability: [TALQ certification] and documented open interfaces.

# 6. Management and maintenance platform

The platform shall manage assets, work orders with SLAs, complaints from residents, night patrols, preventive plans, spares, and reports.

The platform shall work for assets with and without controllers. Controller alarms shall raise work orders automatically.

Reports: share working, SLA met, mean time to repair, repeat failures, energy by circuit, and warranty claims, with export to CSV.

Open API, and full export of all data in an open format at any time and at contract end, at no extra cost.

Platform availability: [99.5]% per month. Support hours: [hours].

# 7. Cybersecurity and data

Unique credentials per device; no shared or default passwords. Encrypted communication. Signed firmware updates.

Role-based access, and a log of all switching commands with user and time.

The authority owns all data. Hosting location: [country / region].

Europe: RED cybersecurity (EN 18031), Cyber Resilience Act, GDPR.  Middle East: TDRA / NCA requirements, local data residency.  South Asia: CERT-In directions, DPDP Act 2023.  USA: NIST IR 8259, applicable state laws.

# 8. Operation and maintenance

Minimum share working: [98]% each month, measured by [controller data / patrols / joint inspection].

Response times: Critical [4] h, High [24] h, Normal [48] h, Low [72] h, from the time the job is raised.

Penalty: [rate] for each light-day dark above the allowed limit. Exclusions: [grid outages, road works, accidents, vandalism above a limit].

Night patrols every [2] weeks on every route. Preventive plan as per Annex B.

Monthly report from the shared platform, agreed by both parties.

# 9. Commissioning and handover

Each controller and node shall be commissioned per the commissioning checklist: asset mapping, location and clock, readings checked against a calibrated meter, switching and dimming tested, one alarm tested.

As-built asset register in the format of the asset import template, with locations, circuits, and serial numbers.

# 10. Local procurement rules

Europe: Directive 2014/24/EU; EU Green Public Procurement criteria for road lighting.  Middle East: local content / in-country value scoring.  South Asia: GeM; Public Procurement (Make in India) Order.  USA: Build America, Buy America (federally funded).

# Annex A — Road types and lighting classes

| Road name / type | Width (m) | Lanes | Pole height (m) | Spacing (m) | Lighting class |
| --- | --- | --- | --- | --- | --- |

# Annex B — Preventive maintenance plan

Use the OpenSLMS preventive maintenance plan template and set intervals for the local climate.